SOURCE CONTROL SPECIFICATION

Part Number: E.SLQ001

Only the item described in this source control to meet the specification listed herein is approved by SILQ.  A substitute item shall not be used without prior approval.

# Purpose

## This document provides the specification for Culligan Portable Exchange Deionizer (PEDI) System.

# Supplier

## Reynolds Culligan, www.reynoldsculligan.com, 119 Franklin Street, West Reading, PA 19611, Tel: (800) 258-4202.

# Manufacturer

## Reynolds Culligan, www.reynoldsculligan.com, 119 Franklin Street, West Reading, PA 19611, Tel: (800) 258-4202.

# Reference Part Number(s)

## Manufacturer Part Name:  Culligan® 14” x 47” Tank Size Portable Exchange Deionizer (PEDI) System

## Manufacturer Model Number:  D-350-MB

# Specification

## Description: Culligan® Portable Exchange Deionizers (PEDI) are a part of a multiple process treatment system that produces high-purity water required for many specialized applications. PEDI systems consist of activated carbon and a selection of high quality ion exchange resins in portable exchange.

## Tank Size: 14 x 47 in.

## Resin Quantity: 3.5 ft3

## Capacity (Grains): 31,500 Grains

## Minimum Flow Rate: 2.0 gpm at 2 psi

## Maximum Flow Rate: 15.0 gpm at 12 psi

## Inlet / Outlet Port: 1” NPT

## Maximum operating parameters

### Pressure: 80 psig

### Temperature: 95℉ (35℃)

### Turbidity: <5 NTU

### Color: <5 Units

### Organics: <3 mg/L

### Free Chlorine: <0.2 mg/L

### Total Dissolved Solids (TDS): <600 mg/L

# System Configuration

## In order to achieve the desired water purity, a minimum of two 14” x 47” D-350-MB tanks are used in series.

## A 1MΩ conductivity sensor is attached to the output of the system where quality of > 1 megaohms (green light) ensures water quality. If conductivity is < 1 megaohms (red light), the tank(s) require servicing.

## After tank change, run approximately 50 gallons through to flush system. Afterwards, take water sample for analytical sampling to ensure water quality meets the high purity water specification outlined in SP-S.SLQ001.

## Connect polyethylene-lined tubing from outlet of PEDI System, as needed, to the High Purity Water Tank Assembly (E.SLQ002).

### Tubing specification: 1” ID x 1-1/4” OD x 1/8” Wall Bev-A-Line® IV Tubing (US Plastics P/N 59519) or equivalent

# Attachments

## Culligan Portable Exchange Deionizers Datasheet