Fume Hood

Operations Manufacturing Procedure

# Purpose

## The purpose of this procedure is to provide instructions on the operation of the fume hood.

# Scope

## This procedure applies to all Silq personnel and subcontractors involved with manufacturing in the Controlled Environment Area (CEA) at the Silq Chico manufacturing facility.

## The Silq Technologies Fume Hood system is equipped with a proofing switch logic system. This system ensures proper fume hood flow prior to allowing work to be safely performed in the manufacturing area. The switch also interlocks mains power to outlets in the work area, allowing work to be conducted if in the up/Operate position.

# Definitions

## Abbreviations / Acronyms

### CEA: Controlled Environment Area

### CFM: Cubic feet per minute

### VAC: Voltage – alternating current

# Responsibilities

## It is the responsibility of Silq personnel and approved applicable contractor personnel to perform their job duties in compliance with the requirements of this procedure

# Procedure: Fume Hood Operation

## Ensure Fume hood curtains are in good condition and provide a seal around the circumference of the fume hood work area.

## Flip the switch “up” to the Operate position. There will be a delay as a sail switch verifies sufficient flow through the hood for operation. Upon completion of this check, all power outlets will be energized for use.

### The diafiltration system will then be able to be turned on.

### All 120VAC outlets will be energized.

### Airflow of the fume hood is set to 350CFM at normal operation conditions.

## Emergency mode

### In the event of a large spill of chemical(s), there is an “EMERGENCY” position on the operation switch, which will increase the fume hood flow to 1450CFM. This mode is intended for use when any process chemicals are spilled from their containers.