Environmental Monitoring

Standard Operating Procedure

# Purpose

## The purpose of this procedure is to establish the methodology for maintaining and monitoring the controlled environment area used for manufacturing Silq product.  This will assure that the environment is maintained in a manner that is suitable to ensure product manufactured at Silq manufacturing facilities meets intended specifications.

# Scope

## This procedure applies to the Silq manufacturing facility in Chico, CA.

# Documents

## Reference Documents

### MP-C.SLQ001		Manufacturing Procedure, Suspension Processing

### SP-S.SLQ001		Source Control Spec, High Purity Water

### QM.SLQ001		Document Control SOP

## Appendices / Associated Forms / Templates

### FM1-QM.SLQ051	Environmental Monitoring Log

# Definitions

## Abbreviations / Acronyms

### CEA: Controlled Environment Area

## General Definitions

### Environmental Monitoring: A set of routing measurements inside the controlled environments for purposes of evaluating the efficiency of environmental controls in place.

### FileHold: Software-based document management system used to electronically store controlled documents.

# Responsibilities

## Operations is responsible for monitoring water quality at defined interval and initiating corrective action(s) when necessary.

## Quality Assurance is responsible for ensuring compliance to the monitoring schedule, reviewing test reports, and documenting excursions from applicable environmental monitoring requirements.

# Procedure: Water Quality

## The water quality of the high purity water source shall be tested periodically to ensure the high purity water meets specifications outlined in SP-S.SLQ001.

## Test frequency

### A contractor shall test the water quality on a semi-annual basis or within 60 days prior to use.

## Sampling locations

### Water samples shall be collected at the output of the Portable Exchange Deionizers (PEDI) system E.SLQ001. See suspension processing system diagram in Appendix A of MP-C.SLQ001.

## Measurements

### The following attributes shall be measured:

#### Iron. Results will be reported as a number of micrograms per liter (µg/L).

#### Zinc. Results will be reported as a number of micrograms per liter (µg/L).

#### Total Dissolved Solids. Results will be reported as number of milligrams per liter (mg/L).

#### Total Organic Carbon. Results will be reported as a number of parts per million (ppm).

## Test requirements

### Attributes shall conform to the following specifications:

#### Iron < 60 µg/L

#### Zinc < 40 µg/L

#### Total Dissolved Solids < 40 mg/L

#### Total Organic Carbon < 1.2 ppm

## Documentation

### The contractor shall record and report the results of the water quality attributes identified in Section 7.4. The report shall include the following:

#### Date of sampling

#### Results/data for water constituents

### Completion of environmental monitoring activity shall be documented on the associated Environmental Monitoring Log (FM1-QM.SLQ051).  This document acts only as a service summary to ensure that the environmental monitoring has been completed according to the testing frequency outlined in Section 6.2.

## Action Limits for Water Quality

### When a result exceeds the allowable threshold, all necessary information on the excursion form in Appendix A shall be completed by QA personnel, Corrective action(s) may be required to address the failure accordingly.

### Product manufactured in the time period associated with the water quality excursion shall be assessed to determine if the excursion impacted conformance to finished product requirements.

# Records Retention

## All records and applicable documentation are filed and maintained by Quality Assurance in the Environmental Monitoring folder as a Quality record in accordance with record retention policies defined in QM.SLQ001, Document Control SOP.

## Records are to be scanned and imported into FileHold and filed within appropriate Environmental Monitoring folder

# Appendix A: Environmental Monitoring Excursion Form

Date: _________________ Failed Area/Location: _____________________ Check Type of Failure: Iron Zinc Total Dissolved Solids Total Organic Carbon

Excursion:

Evaluation:

Corrective Action:

Initiated by: Signature and Date:____________________________________________________________________ Reviewed by: Signature and Date: _____________________________________________________________________